## Totalflow_Carmenita22WA
Description | I/O Name | Type | Field 1 | Field 2 | Field 4 | Read, Write, both or ignore | PID | Storage Unit | Units | Unit Conversion (a) | Unit Conversion (b) | Unit Conversion (c) | Unit Conversion (d) | Low raw value | High raw value | Length | OSDD Channel
Agora Internal Version Click link for template revision notes. Device Name: This column below must be populated below for the system to detect information in that row, however this information is not used in the system. It is a convenient place to add a name/description. The below fields should be populated with a description or name for the IO tag. It is not used in Nimbus. | [6 empty] | 1 = High Freq Live 2 = Medium Freq. Live 3 = Manually Polled Setpoint 4 = High Freq Edge 5 = Medium Freq. Edge 6 = Manually Polled Edge 7 = Edge VRTU Pollset | Production Metric if OSDD or BaseSI |  | storage value = (a*(float)in + b) / (c*(float)in + d) | storage value = (a*(float)in + b) / (c*(float)in + d) | storage value = (a*(float)in + b) / (c*(float)in + d) | storage value = (a*(float)in + b) / (c*(float)in + d)
| Required: This is the IO name displayed in Nimbus. You will see this IO name displayed in telemetry data. Names cannot contain periods. | Required: “UNSIGNED INT”, “FLOAT”, "DISCRETE" or "BOOLEAN”, "INT" or “SIGNED INT”, "BYTE”, "UNSIGNED BYTE”, "DOUBLE”, "LONG” or "SIGNED LONG”, "UNSIGNED LONG" | Required: This defines the type of Modbus register. Discretes=0, Coils=10000, Input=30000, holding=40000 (Example: Modbus addess 40012 or 400012--> Field 1=40000, Field 2=12) | Required: This defines the offest of the Modbus register. These are the offset from the slave device that the gateway will acquire data from. (Example: Modbus addess 40012 or 400012--> Field 1=40000, Field 2=12) | Required: This defines the byte order to read the Modbus IO tag Default is "4321”=big endian "1234”=little endian "3412”=little endian word-swapped "2143”=big endian word-swapped | Required: This defines whether you can read, write or both to an IO. R, W, RW | Required: This is used to classify IO tags into a group so that you can acquire and/or report the data at a specific group time interval. This only defines the groups and not the rates. Default rates defined below. High Feq=1 min reporting, 1 sec acquire; Medium Freq= 5 min reporting, 30 sec acquire; Manually Polled= 1 hour reporting, 60 sec acquire. Internal: PID names above are the default names. PID 1 -3 should remain the deault. You can add PID numbers above 4 with your own name. Example ( 4=My PID) can be configured in this template in column above by adding after the current three choices. | Required for Data Intepretation: These units are displayed in Nimbus next to the data values to define the units. | Required for Data Intepretation: Device Units. This is the units of the raw values streaming from the device Nimbus. These values are stored in Nimbus database. Units will equal Storage Units when there is no Unit Conversion. | Internal Use: Optional but column headers required for upload validation. The 4 unit conversion fields (a,b,c,d) are for scaling purposes. They are all used together to give flexibility in scaling raw values from a device to show final scaled values in Nimbus. This scaling is done only in Nimbus and not on the Gateway. Values stored in the Nimbus database will be the result of these formulas. Storage Units should always define values displayed in Nimbus. Units define the (Example: ) | Internal Use:See Unit Conversion(a) details. | Internal Use:See Unit Conversion(a) details. | Internal Use:See Unit Conversion(a) details. | Optional: Stored in Nimbus database for information but not used by the system. | Optional: Stored in Nimbus database for information but not used by the system. | Optional Internal Use Only: this is used for vector IO. This number signifies the number of IO to query starting at the Modbus register specified in Field 1 & 2. | Internal Use Only Optional: Open Schlumberger Data Dictionary : This is stored in Nimbus as part of the device configuration.
22-WA Flow Rate | GLIR | UNSIGNED INT | 40000 | 1 | 4321 | R | 2 | MCF/Day
22-WA Last Calculated Period Volume | 22-WA Last Calculated Period Volume | UNSIGNED INT | 40000 | 2 | 4321 | R | 2 | SCF
22-WA Accumulation Volume | 22-WA Accumulation Volume | UNSIGNED INT | 40000 | 3 | 4321 | R | 2 | MCF
22-WA Todays Volume | 22-WA Today Volume | UNSIGNED INT | 40000 | 4 | 4321 | R | 2 | MCF
22-WA Yesterdays Volume | 22-WA Yesterday Volume | UNSIGNED INT | 40000 | 5 | 4321 | R | 2 | MCF
22-WA Static Pressure | 22-WA Static Pressure | UNSIGNED INT | 40000 | 6 | 4321 | R | 2 | Psi
22-WA Differencial Pressure | 22-WA Differencial Pressure | UNSIGNED INT | 40000 | 7 | 4321 | R | 2 | Psi | Raw=(PSIA*10000/276799) | 10000 | 0 | 0 | 276799
Line Temperature | 22-WA Line Temperature | UNSIGNED INT | 40000 | 8 | 4321 | R | 2 | F
20-WB Flow Rate | GLIR | UNSIGNED INT | 40000 | 9 | 4321 | R | 2 | MCF/Day
20-WB Last Calculated Period Volume | 20-WB Last Calculated Period Volume | UNSIGNED INT | 40000 | 10 | 4321 | R | 2 | SCF
20-WB Accumulation Volume | 20-WB Accumulation Volume | UNSIGNED INT | 40000 | 11 | 4321 | R | 2 | MCF
20-WB Todays Volume | 20-WB Today Volume | UNSIGNED INT | 40000 | 12 | 4321 | R | 2 | MCF
20-WBYesterdays Volume | 20-WB Yesterday Volume | UNSIGNED INT | 40000 | 13 | 4321 | R | 2 | MCF
20-WB Static Pressure | 20-WB Static Pressure | UNSIGNED INT | 40000 | 14 | 4321 | R | 2 | Psia
20-WB Differencial Pressure | 20-WB Differencial Pressure | UNSIGNED INT | 40000 | 15 | 4321 | R | 2 | Psi | Raw=(PSIA*10000/276799) | 10000 | 0 | 0 | 276799
20-WB Line Temperature | 20-WB Line Temperature | UNSIGNED INT | 40000 | 16 | 4321 | R | 2 | F
24-LS Flow Rate | GLIR B | UNSIGNED INT | 40000 | 17 | 4321 | R | 2 | MCF/Day
24-LS Last Calculated Period Volume | 24-LS Last Calculated Period Volume | UNSIGNED INT | 40000 | 18 | 4321 | R | 2 | SCF
24-LS Accumulation Volume | 24-LS Accumulation Volume | UNSIGNED INT | 40000 | 19 | 4321 | R | 2 | MCF
24-LS Todays Volume | 24-LS Today Volume | UNSIGNED INT | 40000 | 20 | 4321 | R | 2 | MCF
24-LS Yesterdays Volume | 24-LS Yesterday Volume | UNSIGNED INT | 40000 | 21 | 4321 | R | 2 | MCF
24-LS Static Pressure | 24-LS Static Pressure | UNSIGNED INT | 40000 | 22 | 4321 | R | 2 | Psia
24-LS Differencial Pressure | 24-LS Differencial Pressure | UNSIGNED INT | 40000 | 23 | 4321 | R | 2 | Psi | Raw=(PSIA*10000/276799) | 10000 | 0 | 0 | 276799
24-LS Line Temperature | 24-LS Line Temperature | UNSIGNED INT | 40000 | 24 | 4321 | R | 2 | F
Battery Voltage | Total Flow Battery Voltage | UNSIGNED INT | 40000 | 25 | 4321 | R | 2 | V
22-WA Flow Setpoint | 22-WA Injection Setpoint | UNSIGNED INT | 40000 | 26 | 4321 | RW | 2 | MCF/Day
22-WA Flow High Setpoint | 22-WA Flow High Setpoint | UNSIGNED INT | 40000 | 27 | 4321 | RW | 2 | MCF/Day
22-WA Flow Low Setpoint | 22-WA Flow Low Setpoint | UNSIGNED INT | 40000 | 28 | 4321 | RW | 2 | MCF/Day
22-WA Flow Deadband | 22-WA Flow Deadband | UNSIGNED INT | 40000 | 29 | 4321 | RW | 2
22-WA Flow Gain | 22-WA Flow Gain | UNSIGNED INT | 40000 | 30 | 4321 | RW | 2
20-WB Flow Setpoint | 20-WB Injection Setpoint | UNSIGNED INT | 40000 | 31 | 4321 | RW | 2 | MCF/Day
20-WB Flow High Setpoint | 20-WB Flow High Setpoint | UNSIGNED INT | 40000 | 32 | 4321 | RW | 2 | MCF/Day
20-WB Flow Low Setpoint | 20-WB Flow Low Setpoint | UNSIGNED INT | 40000 | 33 | 4321 | RW | 2 | MCF/Day
20-WB Flow Deadband | 20-WB Flow Deadband | UNSIGNED INT | 40000 | 34 | 4321 | RW | 2
20-WB Flow Gain | 20-WB Flow Gain | UNSIGNED INT | 40000 | 35 | 4321 | RW | 2
24-LS Injection Setpoint | 24-LS Injection Setpoint | UNSIGNED INT | 40000 | 36 | 4321 | RW | 2 | MCF/Day
24-LS Flow High Setpoint | 24-LS Flow High Setpoint | UNSIGNED INT | 40000 | 37 | 4321 | RW | 2 | MCF/Day
24-LS Flow Low Setpoint | 24-LS Flow Low Setpoint | UNSIGNED INT | 40000 | 38 | 4321 | RW | 2 | MCF/Day
24-LS Flow Deadband | 24-LS Flow Deadband | UNSIGNED INT | 40000 | 39 | 4321 | RW | 2
24-LS Flow Gain | 24-LS Flow Gain | UNSIGNED INT | 40000 | 40 | 4321 | RW | 2
22-WA Gas Injection Valve Postion | 22-WA Gas Injection Valve Postion | UNSIGNED INT | 40000 | 41 | 4321 | R | 2 | % | Raw=(%/100) | 1 | 0 | 0 | 100
20-WB Gas Injection Valve Postion | 20-WB Gas Injection Valve Postion | UNSIGNED INT | 40000 | 42 | 4321 | R | 2 | % | Raw=(%/100) | 1 | 0 | 0 | 100
24-LS Gas Injection Valve Postion | 24-LS Gas Injection Valve Postion | UNSIGNED INT | 40000 | 43 | 4321 | R | 2 | % | Raw=(%/100) | 1 | 0 | 0 | 100
Note on B1: Obed Gutierrez: sensor type